## Client Data and Q's
Stack description | Source | Activity | Abatement | Location | Height Of Stack/emmission Point | Diameter (m) | Release rate (efflux velocity, m/s) | Total flow (m3/hr) | Substance emission concentrations mg/m3 | Plant Served | Substance / Notes | SLR Questions
LEV-E-07 | AREA E - Anode Mixing / Coating | Anode - preparation of coating mixture | HEPA ? | West elevation Harbour | Terminates 3m above roof | 0.355 | 11.5 | 6600 | < 2mg/m³ | 1 x E14, 1x E30 | DI Water, Graphite, CMP and SP <2 mg/m³ | Please confirm what CMP and SP stand for. Why has an emission limit of <2mg/m³ been applied to this emission point? What pollutant species will be being emitted at this concentration? We understood this to be a water based process with no VOC present. Confirm what abatement will be present - Will this be via HEPA filters for Dust abatement?
LEV-E-05 | Area E - Anode Mixing | Anode - preparation of coating mixture | HEPA ? | West elevation Harbour | Terminates 3m above roof | 0.3 | 13.7 | 3851 | < 2mg/m³ | 9xE11, 5xE15 | DI Water, Graphite, CMP and SP <2 mg/m³ | As Above
LEV-E-09 | Area E - Anode Coater | Anode coating | None? | West elevation Harbour | Terminates 3m above roof | 0.3 | 14.2 | 2557 | < 2mg/m³ | 4xE22,2xE22.1, 2xE23,5xE21, 3xE21.1,1xE30 | Water solvent present | Why has an emission limit of <2mg/m³ been applied to this emission point? What pollutant species would be present? We understood this to be a water based process with no VOC present.
LEV-E-04 | Area E - Cathode mixing | Cathode - preparation of coating mixture | HEPA ? | West elevation Harbour | Terminates 3m above roof | 0.3 | 13.8 | 3860 | NMP @ < 2mg/m3 | 8xE6, 4x E10, 2xE8 | Includes Nickel, Copper fume (as Cu) =< 2 mg/m³ | Please confirm whether nickel / copper fume will actually be present, and is the emission level of <2mg/m³ relevant to Nickel and Copper? Confirm what abatement will be present - Will this be via HEPA filters for Dust / metal particulate abatement?
LEV-E-10 | Area E Cathode Press | Cathode - production |  | North elevation Harbour | Terminates 3m above roof | 0.15 | 11.4 | 630 | Hot Air Only | E37 x 3 | Hot Air Only
LEV-E-06 | Area E - Cathode mixing / Coating | Cathode - coating | 2 stage condensation and adsorption Wheel | North elevation Harbour | Terminates 3m above roof | 0.45 | 11.5 | 6600 | NMP @ < 2mg/m3 | E25 x1, E9 x 1 | NMP
LEV-E-08 | Area E - Cathode Coater | Cathode - Coating | 2 stage condensation and adsorption Wheel | North elevation Harbour | Terminate 3m above roof | 0.45 | 15.7 | 3482 | NMP @ < 2mg/m3 | 4xE16,2xE16.1, 8xE17,4xE17.1,2xE18,4xE19,4xE19.1,1xE25 | NMP
LEV-A-06 | Area A - Cell - Roll Bake | ? | None? | North elevation Harbour | Terminates 3m above roof | 0.355 | 11.3 | 5120 | traces of water vapour | 4 x C2 | Water Vapour
LEV-B-01 | Area B - De-gas Roll Press | ? | None? | North elevation Harbour | Terminates 3m above roof | 0.355 | 11.3 | 3900 | DEC @ < 10 mg/m3 , EC @ < 8 mg/ m3 | 4 x C11, 4 x C12 | Requested LEV report and stack emission monitoring to confirm. | Please confirm - will DEC and EC actually be present in this process area?
LEV-C-01 | Area C - Glue Module | Cell assembly and cell pouch bonding | None? | East Elevation Harbour | Terminates 3m above roof | 1 | 11.9 | 6789 | < 2mg/m³ | 1 x M2 | Ozone, Carbon monoxide, Nitrogen oxide potential for MIG. Additional potential for argon and helium if TIG Structural glue 211221 TDS_BETAFORCE CB-2 contains isocyanates. | Why has an emission limit of <2mg/m³ been applied to this emission point? What pollutant species are expected to be present and will they be at concentrations up to 2 mg/m³? The structural glue is a 2 part composite bonding adhesive, please provide the MSDS so we can confirm what could potentially be emitted to air.
LEV-C-02 | Area C - Glue Module | Cell assembly and cell pouch bonding | None? | East Elevation Harbour | Terminates 3m above roof | 1 | 11.9 | 6790 | < 2mg/m³ | 2 x M2 | Ozone, Carbon monoxide, Nitrogen oxide potential for MIG. Additional potential for argon and helium if TIG Structural glue 211221 TDS_BETAFORCE CB-2 contains isocyanates. | As Above
LEV-C-03 | Area C - Glue Module | Cell assembly and cell pouch bonding | None? | East Elevation Harbour | Terminates 3m above roof | 1 | 11.9 | 6791 | < 2mg/m³ | 3 x M2 | Ozone, Carbon monoxide, Nitrogen oxide potential for MIG. Additional potential for argon and helium if TIG Structural glue 211221 TDS_BETAFORCE CB-2 contains isocyanates. | As Above
LEV-C-04 | Area C - Glue Module | Cell assembly and cell pouch bonding | None? | East Elevation Harbour | Terminates 3m above roof | 1 | 11.9 | 6792 | < 2mg/m³ | 4 x M2 | Ozone, Carbon monoxide, Nitrogen oxide potential for MIG. Additional potential for argon and helium if TIG Structural glue 211221 TDS_BETAFORCE CB-2 contains isocyanates. | As Above
LEV-A-04 | Area A - Injection | Battery filling with electrolyte | None? | Central Core | Terminates 3m above roof | 0.56 | 14 | 15660 | DEC @ < 20 mg/m3 , EC @ < 15 mg/ m3 | 4 x C9 | Requested LEV report and stack emission monitoring to confirm.
LEV-A-05 | Area A - Injection (Cromex Kit) | Battery filling with electrolyte | None? | Central Core | Terminates 3m above roof | 0.63 | 11.3 | 8010 | < 2mg/m³ | 1 x Filter Cab, 1 x Manifold, 1 x Cleaning Cab, 4 x POS | NMP | Please advise - will NMP actually be present in this plant area? We understood this to be handling Electrolyte (DEC / EC only). In which case should the emissions be DEC @ < 20 mg/m3 , EC @ < 15 mg/ m3
CMP |  |  | Anode production only | Please advise the full name of this material
SP |  |  | Anode production only | Please advise the full name of this material
NMP | N-methyl-2-pyrrolidone |  | Cathode production only
DEC | Diethyl Carbonate |  | Within electrolyte and used for cleaning the electrolyte system
EC | Ethyl Carbonate |  | Within electrolyte
IPA | Isopropyl Alcohol |  | plant cleaning | Please advise where IPA and Acetone will be used in the plant, and which emission points any vapour emissions could potentially be vented via.
Acetone | Acetone |  | plant cleaning
Fermapor K31 |  |  | polyurethane sealing foam / fast cure gaskets.
Bergquist TGF2200 |  |  | BERGQUIST® GAP FILLER TGF 2200 APS is a two component, thermally conductive silicone based liquid gap filler.
Data excludes south side of plant

## Emissions Data North
| Plant 2 North |  |  | Data provided by AESC Engineerng Team |  | Note: Emission points A1 - A6 are allocated to the Boiler Plant which is covered by a separate MCP Permit
Emission Point Reference | Stack Description | Source Type | Source | Activity | Abatement | Location | Height Of Stack/Emission Point (m) | Diameter (m) | Release Rate (efflux velocity, m/s) | Total flow (m³/hr) | Substance Emission Concentrations mg/Nm³ | Emission Concentration (mg/Nm³) | Calculated Hourly Mass Emission (kg/hour) | Substance / Notes | Identification of Applicable BAT AEL | Emissions Monitoring Requirements
A7 | LEV-E-07 | Area LEV | AREA E - Anode Mixing / Coating | Anode - preparation of coating mixture | Air extraction Via HEPA filters for abatement of Particulates | West elevation Harbour | 33m Terminates 3m above roof | 0.45 | 11.5 | 6600 | No Significant Pollutants | N/A | N/A | No VOC use in this area. The mixing process includes Deionised Water, Graphite, Carboxy Methyl Cellulose (CMC) and Carbon Black Powder (SP), however this is an enclosed process with no particulate emissions to air expected. HEPA filters on the process area LEV outlet have been provided as a precautionary measure. | None | None
A8 | LEV-E-05 | Area LEV | Area E - Anode Mixing | Anode - preparation of coating mixture | Air extraction Via HEPA filters for abatement of Particulates | West elevation Harbour | 33m Terminates 3m above roof | 0.315 | 13.7 | 3851 | No Significant Pollutants | N/A | N/A | No VOC use in this area. The mixing process includes Deionised Water, Graphite, Carboxy Methyl Cellulose (CMC) and Carbon Black Powder (SP), however this is an enclosed process with no particulate emissions to air expected. HEPA filters on the process area LEV outlet have been provided as a precautionary measure. | None | None
A9 | LEV-E-09 | Process Vent | Area E - Anode Coaters - combined emissions from 2 lines | Anode coating | None | West elevation Harbour | 33m Terminates 3m above roof | 0.25 | 14.2 | 2557 | No Significant Pollutants | N/A | N/A | Water Vapour only | None | None
A10 | LEV-E-04 | Area LEV | Area E - Cathode mixing | Cathode - preparation of coating mixture | Air extraction Via HEPA filters for abatement of Particulates | West elevation Harbour | 33m Terminates 3m above roof | 0.315 | 13.8 | 3860 | NMP @ < 2mg/m3 | 2 | 0.00772 | N-methyl-2-pyrrolidone (NMP) The mixing process includes the use of NMP, and Lithium, Nickel, Cobalt, Aluminium Oxides, however this is an enclosed process with no particulate emissions to air expected. HEPA filters on the process area LEV outlet have been provided as a precautionary measure. | NMP (CMR 1) <1 - 5 mg/Nm³ | Emission level is <10 kgC/hour Periodic sampling for TVOC once per year EN 12619
A11 | LEV-E-10 | Area LEV | Area E Cathode Press | Cathode - production | None | North elevation Harbour | 33m Terminates 3m above roof | 0.14 | 11.4 | 630 | No Significant Pollutants Hot Air Only | N/A | N/A | Hot Air Only | None | None
A12 | LEV-E-06 | Area LEV | Area E - Cathode mixing / Coating | Cathode - coating | Air extraction Via HEPA filters for abatement of Particulates | North elevation Harbour | 33m Terminates 3m above roof | 0.45 | 11.5 | 6600 | NMP @ < 2mg/m3 | 2 | 0.0132 | N-methyl-2-pyrrolidone (NMP) | NMP (CMR 1) <1 - 5 mg/Nm³ | Emission level is <10 kgC/hour Periodic sampling for TVOC once per year EN 12619
A13 | LEV-E-08 | Process Vent | Area E - Cathode Coaters - combined emissions from 2 lines | Cathode - Coating | 2 stage condensation and 2 stage zeolite adsorption wheels with thermal desorption and condensation | North elevation Harbour | 33m Terminates 3m above roof | 0.28 | 15.7 | 3482 | NMP @ < 2mg/m3 | 2 | 0.006964 | N-methyl-2-pyrrolidone (NMP) | NMP (CMR 1) <1 - 5 mg/Nm³ | Emission level is <10 kgC/hour Periodic sampling for TVOC once per year EN 12619
A14 | LEV-A-06 | Area LEV | Area A - Cell - Roll Bake | Cell Roll Bake | None | North elevation Harbour | 33m Terminates 3m above roof | 0.45 | 11.3 | 5120 | No Significant Pollutants Traces of water vapour | N/A | N/A | Water Vapour Note that flow and velocity data currently do not align, but this emission point wil not be included in any modelling assessment as it does not release potential pollutants. | None | None
A15 | LEV-B-01 | Area LEV | Area B - De-gas Roll Press | Degassing Roll Press | None | North elevation Harbour | 19m Terminates 3m above roof | 0.35 | 11.3 | 3900 | Possibility for VOC vapour from electrolyte within slit cell Diethyl Carbonate (DEC) Ethylene Carbonate (EC) Ethyl Methyl Carbonate (EMC) Assess as TVOC at <20 mg/m³ | 20 | 0.078 | The degas process doesn’t use Electrolyte or Diethyl Carbonate (DEC) as a raw material. However, there is limited potential for trace DEC, EC and EMC to be drawn into the air extract system from the slit cell when it is in the chamber. The level of VOC likely to be present will be very low indeed, but as a precautionary measure it has been assumed that the emission could include up to 20 mg/m³ at total VOC. | Total VOC with a mass emission rate of <100g/h No BAT-AEL applies | Emission level is <10 kgC/hour and <0.1 kg/hour BAT requirement is for periodic sampling for TVOC once every 3 years EN 12619 It is proposed that an initial confirmatory sampling assessment be undertaken to assess whether any VOC is emited via this LEV, and if no VOC is identified then no further monitoring be undertaken.
A16 | LEV-C-01 | Area LEV | Area C - Glue Module | Cell assembly and cell pouch bonding | None | East Elevation Harbour | 19m Terminates 3m above roof | 0.45 | 11.9 | 6789 | Trace VOC Assess as TVOC at <2mg/m³ | 2 | 0.013578 | Most glues are 2 part (Resin and Hardener) in paste or viscous liquid form and are kept within sealed containers until used. Glues generally have no VOC content, although the Thermal Glue resin does include 1 - 5% of petroleum which would be a VOC, but only present at very low concentrations. MIG welding is undertaken in this area which would generate low concentrations of Ozone, Carbon monoxide and Nitrogen oxide. TIG welding is also undertaken in this area which has the potential to generate low concentrations of argon and helium. No assessment of gases generated by welding is proposed as emission levels are anticipated to be low and will occur intermittently. | Total VOC with a mass emission rate of <100g/h No BAT-AEL applies | Emission level is <10 kgC/hour and <0.1 kg/hour BAT requirement is for periodic sampling for TVOC once every 3 years EN 12619 It is proposed that an initial confirmatory sampling assessment be undertaken to assess whether any VOC is emited via this LEV, and if no VOC is identified then no further monitoring be undertaken.
A17 | LEV-C-02 | Area LEV | Area C - Glue Module | Cell assembly and cell pouch bonding | None | East Elevation Harbour | 19m Terminates 3m above roof | 0.45 | 11.9 | 6790 | Trace VOC Assess as TVOC at <2mg/m³ | 2 | 0.01358 | Most glues are 2 part (Resin and Hardener) in paste or viscous liquid form and are kept within sealed containers until used. Glues generally have no VOC content, although the Thermal Glue resin does include 1 - 5% of petroleum which would be a VOC, but only present at very low concentrations. MIG welding is undertaken in this area which would generate low concentrations of Ozone, Carbon monoxide and Nitrogen oxide. TIG welding is also undertaken in this area which has the potential to generate low concentrations of argon and helium. No assessment of gases generated by welding is proposed as emission levels are anticipated to be low and will occur intermittently. | Total VOC with a mass emission rate of <100g/h No BAT-AEL applies | Emission level is <10 kgC/hour and <0.1 kg/hour Periodic sampling for TVOC once every 3 years EN 12619 It is proposed that an initial confirmatory sampling assessment be undertaken to assess whether any VOC is emited via this LEV, and if no VOC is identified then no further monitoring be undertaken.
A18 | LEV-C-03 | Area LEV | Area C - Glue Module | Cell assembly and cell pouch bonding | None | East Elevation Harbour | 19m Terminates 3m above roof | 0.45 | 11.9 | 6791 | Trace VOC Assess as TVOC at <2mg/m³ | 2 | 0.013582 | Most glues are 2 part (Resin and Hardener) in paste or viscous liquid form and are kept within sealed containers until used. Glues generally have no VOC content, although the Thermal Glue resin does include 1 - 5% of petroleum which would be a VOC, but only present at very low concentrations. MIG welding is undertaken in this area which would generate low concentrations of Ozone, Carbon monoxide and Nitrogen oxide. TIG welding is also undertaken in this area which has the potential to generate low concentrations of argon and helium. No assessment of gases generated by welding is proposed as emission levels are anticipated to be low and will occur intermittently. | Total VOC with a mass emission rate of <100g/h No BAT-AEL applies | Emission level is <10 kgC/hour and <0.1 kg/hour BAT requirement is for periodic sampling for TVOC once every 3 years EN 12619 It is proposed that an initial confirmatory sampling assessment be undertaken to assess whether any VOC is emited via this LEV, and if no VOC is identified then no further monitoring be undertaken.
A19 | LEV-C-04 | Area LEV | Area C - Glue Module | Cell assembly and cell pouch bonding | None | East Elevation Harbour | 19m Terminates 3m above roof | 0.45 | 11.9 | 6792 | Trace VOC Assess as TVOC at <2mg/m³ | 2 | 0.013584 | Most glues are 2 part (Resin and Hardener) in paste or viscous liquid form and are kept within sealed containers until used. Glues generally have no VOC content, although the Thermal Glue resin does include 1 - 5% of petroleum which would be a VOC, but only present at very low concentrations. MIG welding is undertaken in this area which would generate low concentrations of Ozone, Carbon monoxide and Nitrogen oxide. TIG welding is also undertaken in this area which has the potential to generate low concentrations of argon and helium. No assessment of gases generated by welding is proposed as emission levels are anticipated to be low and will occur intermittently. | Total VOC with a mass emission rate of <100g/h No BAT-AEL applies | Emission level is <10 kgC/hour and <0.1 kg/hour BAT requirement is for periodic sampling for TVOC once every 3 years EN 12619 It is proposed that an initial confirmatory sampling assessment be undertaken to assess whether any VOC is emited via this LEV, and if no VOC is identified then no further monitoring be undertaken.
A20 | LEV-A-04 | Area LEV | Area A - Injection | Battery filling with electrolyte - Injection Systems | None | Central Core | 33m Terminates 3m above roof | 0.63 | 14 | 15660 | VOC Vapour from Electrolyte processing containing Diethyl Carbonate (DEC) Ethylene Carbonate (EC) Ethyl Methyl Carbonate (EMC) Assess as TVOC at <20 mg/m³ | 20 | 0.3132 | Volatile Components of Electrolyte i.e. Diethyl Carbonate (DEC) (3 - 10% of electrolyte) Ethylene Carbonate (EC) (20 - 30% of electrolyte) Ethyl Methyl Carbonate (EMC) (50 - 60% of electrolyte) | TVOC with a mass emission rate of >100g/h 1 - 20 mgC/Nm³ | Emission level is <10 kgC/hour Periodic sampling for TVOC once per year EN 12619
A21 | LEV-A-05 | Area LEV | Area A - Injection (Cromex Kit) | Battery filling with electrolyte - Injection Systems | None | Central Core | 33m Terminates 3m above roof | 0.5 | 11.3 | 8010 | VOC Vapour from Electrolyte processing containing Diethyl Carbonate (DEC) Ethylene Carbonate (EC) Ethyl Methyl Carbonate (EMC) Assess as TVOC at <20 mg/m³ | 20 | 0.1602 | Volatile Components of Electrolyte i.e. Diethyl Carbonate (DEC) (3 - 10% of electrolyte) Ethylene Carbonate (EC) (20 - 30% of electrolyte) Ethyl Methyl Carbonate (EMC) (50 - 60% of electrolyte) | TVOC with a mass emission rate of >100g/h 1 - 20 mgC/Nm³ | Emission level is <10 kgC/hour Periodic sampling for TVOC once per year EN 12619

## Emissions Data South
Plant 2 - South
Emission Point Reference | Stack description (assumed to be as per North Plant) | Source Type | Source (assumed to be as per North Plant) | Activity | Abatement | Location | Height Of Stack/Emission Point (m) | Diameter (m) | Release Rate (efflux velocity, m/s) | Total flow (m³/hr) | Substance Emission Concentrations mg/Nm³ | Emission Concentration (mg/Nm³) | Calculated Hourly Mass Emission (kg/hour) | Substance / Notes | Identification of Applicable BAT AEL | Emissions Monitoring Requirements
A27 | LEV-E-07S | Area LEV | AREA E - Anode Mixing / Coating | Anode - preparation of coating mixture | Air extraction Via HEPA filters for abatement of Particulates | West elevation Harbour | 33m Terminates 3m above roof | 0.45 | 11.5 | 6600 | No Significant Pollutants | N/A | N/A | No VOC use in this area. The mixing process includes Deionised Water, Graphite, Carboxy Methyl Cellulose (CMC) and Carbon Black Powder (SP), however this is an enclosed process with no particulate emissions to air expected. HEPA filters on the process area LEV outlet have been provided as a precautionary measure. | None | None
A28 | LEV-E-05S | Area LEV | Area E - Anode Mixing | Anode - preparation of coating mixture | Air extraction Via HEPA filters for abatement of Particulates | West elevation Harbour | 33m Terminates 3m above roof | 0.315 | 13.7 | 3851 | No Significant Pollutants | N/A | N/A | No VOC use in this area. The mixing process includes Deionised Water, Graphite, Carboxy Methyl Cellulose (CMC) and Carbon Black Powder (SP), however this is an enclosed process with no particulate emissions to air expected. HEPA filters on the process area LEV outlet have been provided as a precautionary measure. | None | None
A29 | LEV-E-09S | Process Vent | Area E - Anode Coater | Anode coating | None | West elevation Harbour | 33m Terminates 3m above roof | 0.25 | 14.2 | 2557 | No Significant Pollutants | N/A | N/A | Water Vapour only | None | None
A30 | LEV-E-04S | Area LEV | Area E - Cathode mixing | Cathode - preparation of coating mixture | Air extraction Via HEPA filters for abatement of Particulates | West elevation Harbour | 33m Terminates 3m above roof | 0.315 | 13.8 | 3860 | NMP @ < 2mg/m3 | 2 | 0.00772 | N-methyl-2-pyrrolidone (NMP) The mixing process includes the use of NMP, and Lithium, Nickel, Cobalt, Aluminium Oxides, however this is an enclosed process with no particulate emissions to air expected. HEPA filters on the process area LEV outlet have been provided as a precautionary measure. | NMP (CMR 1) <1 - 5 mg/Nm³ | Emission level is <10 kgC/hour Periodic sampling for TVOC once per year EN 12619
A31 | LEV-E-10S | Area LEV | Area E Cathode Press | Cathode - production | None | North elevation Harbour | 33m Terminates 3m above roof | 0.14 | 11.4 | 630 | No Significant Pollutants Hot Air Only | N/A | N/A | Hot Air Only | None | None
A32 | LEV-E-06S | Area LEV | Area E - Cathode mixing / Coating | Cathode - coating | Air extraction Via HEPA filters for abatement of Particulates | North elevation Harbour | 33m Terminates 3m above roof | 0.45 | 11.5 | 6600 | NMP @ < 2mg/m3 | 2 | 0.0132 | N-methyl-2-pyrrolidone (NMP) | NMP (CMR 1) <1 - 5 mg/Nm³ | Emission level is <10 kgC/hour Periodic sampling for TVOC once per year EN 12619
A33 | LEV-E-08S | Process Vent | Area E - Cathode Coater | Cathode - Coating | 2 stage condensation and 2 stage zeolite adsorption wheels with thermal desorption and condensation | North elevation Harbour | 33m Terminates 3m above roof | 0.28 | 15.7 | 3482 | NMP @ < 2mg/m3 | 2 | 0.006964 | N-methyl-2-pyrrolidone (NMP) | NMP (CMR 1) <1 - 5 mg/Nm³ | Emission level is <10 kgC/hour Periodic sampling for TVOC once per year EN 12619
A34 | LEV-A-06S | Area LEV | Area A - Cell - Roll Bake | Cell Roll Bake | None | North elevation Harbour | 33m Terminates 3m above roof | 0.45 | 11.3 | 5120 | No Significant Pollutants Traces of water vapour | N/A | N/A | Water Vapour Note that flow and velocity data currently do not align, but this emission point wil not be included in any modelling assessment as it does not release potential pollutants. | None | None
A35 | LEV-B-01S | Area LEV | Area B - De-gas Roll Press | Degassing Roll Press | None | North elevation Harbour | 19m Terminates 3m above roof | 0.35 | 11.3 | 3900 | Possibility for VOC vapour from electrolyte within slit cell Diethyl Carbonate (DEC) Ethylene Carbonate (EC) Ethyl Methyl Carbonate (EMC) Assess as TVOC at <20 mg/m³ | 20 | 0.078 | The degas process doesn’t use Electrolyte or Diethyl Carbonate (DEC) as a raw material. However, there is limited potential for trace DEC, EC and EMC to be drawn into the air extract system from the slit cell when it is in the chamber. The level of VOC likely to be present will be very low indeed, but as a precautionary measure it has been assumed that the emission could include up to 20 mg/m³ at total VOC. | Total VOC with a mass emission rate of <100g/h No BAT-AEL applies | Emission level is <10 kgC/hour and <0.1 kg/hour BAT requirement is for periodic sampling for TVOC once every 3 years EN 12619 It is proposed that an initial confirmatory sampling assessment be undertaken to assess whether any VOC is emited via this LEV, and if no VOC is identified then no further monitoring be undertaken.
A36 | LEV-C-01S | Area LEV | Area C - Glue Module | Cell assembly and cell pouch bonding | None | East Elevation Harbour | 19m Terminates 3m above roof | 0.45 | 11.9 | 6789 | Trace VOC Assess as TVOC at <2mg/m³ | 2 | 0.013578 | Most glues are 2 part (Resin and Hardener) in paste or viscous liquid form and are kept within sealed containers until used. Glues generally have no VOC content, although the Thermal Glue resin does include 1 - 5% of petroleum which would be a VOC, but only present at very low concentrations. MIG welding is undertaken in this area which would generate low concentrations of Ozone, Carbon monoxide and Nitrogen oxide. TIG welding is also undertaken in this area which has the potential to generate low concentrations of argon and helium. No assessment of gases generated by welding is proposed as emission levels are anticipated to be low and will occur intermittently. | Total VOC with a mass emission rate of <100g/h No BAT-AEL applies | Emission level is <10 kgC/hour and <0.1 kg/hour BAT requirement is for periodic sampling for TVOC once every 3 years EN 12619 It is proposed that an initial confirmatory sampling assessment be undertaken to assess whether any VOC is emited via this LEV, and if no VOC is identified then no further monitoring be undertaken.
A37 | LEV-C-02S | Area LEV | Area C - Glue Module | Cell assembly and cell pouch bonding | None | East Elevation Harbour | 19m Terminates 3m above roof | 0.45 | 11.9 | 6790 | Trace VOC Assess as TVOC at <2mg/m³ | 2 | 0.01358 | Most glues are 2 part (Resin and Hardener) in paste or viscous liquid form and are kept within sealed containers until used. Glues generally have no VOC content, although the Thermal Glue resin does include 1 - 5% of petroleum which would be a VOC, but only present at very low concentrations. MIG welding is undertaken in this area which would generate low concentrations of Ozone, Carbon monoxide and Nitrogen oxide. TIG welding is also undertaken in this area which has the potential to generate low concentrations of argon and helium. No assessment of gases generated by welding is proposed as emission levels are anticipated to be low and will occur intermittently. | Total VOC with a mass emission rate of <100g/h No BAT-AEL applies | Emission level is <10 kgC/hour and <0.1 kg/hour Periodic sampling for TVOC once every 3 years EN 12619 It is proposed that an initial confirmatory sampling assessment be undertaken to assess whether any VOC is emited via this LEV, and if no VOC is identified then no further monitoring be undertaken.
A38 | LEV-C-03S | Area LEV | Area C - Glue Module | Cell assembly and cell pouch bonding | None | East Elevation Harbour | 19m Terminates 3m above roof | 0.45 | 11.9 | 6791 | Trace VOC Assess as TVOC at <2mg/m³ | 2 | 0.013582 | Most glues are 2 part (Resin and Hardener) in paste or viscous liquid form and are kept within sealed containers until used. Glues generally have no VOC content, although the Thermal Glue resin does include 1 - 5% of petroleum which would be a VOC, but only present at very low concentrations. MIG welding is undertaken in this area which would generate low concentrations of Ozone, Carbon monoxide and Nitrogen oxide. TIG welding is also undertaken in this area which has the potential to generate low concentrations of argon and helium. No assessment of gases generated by welding is proposed as emission levels are anticipated to be low and will occur intermittently. | Total VOC with a mass emission rate of <100g/h No BAT-AEL applies | Emission level is <10 kgC/hour and <0.1 kg/hour BAT requirement is for periodic sampling for TVOC once every 3 years EN 12619 It is proposed that an initial confirmatory sampling assessment be undertaken to assess whether any VOC is emited via this LEV, and if no VOC is identified then no further monitoring be undertaken.
A39 | LEV-C-04S | Area LEV | Area C - Glue Module | Cell assembly and cell pouch bonding | None | East Elevation Harbour | 19m Terminates 3m above roof | 0.45 | 11.9 | 6792 | Trace VOC Assess as TVOC at <2mg/m³ | 2 | 0.013584 | Most glues are 2 part (Resin and Hardener) in paste or viscous liquid form and are kept within sealed containers until used. Glues generally have no VOC content, although the Thermal Glue resin does include 1 - 5% of petroleum which would be a VOC, but only present at very low concentrations. MIG welding is undertaken in this area which would generate low concentrations of Ozone, Carbon monoxide and Nitrogen oxide. TIG welding is also undertaken in this area which has the potential to generate low concentrations of argon and helium. No assessment of gases generated by welding is proposed as emission levels are anticipated to be low and will occur intermittently. | Total VOC with a mass emission rate of <100g/h No BAT-AEL applies | Emission level is <10 kgC/hour and <0.1 kg/hour BAT requirement is for periodic sampling for TVOC once every 3 years EN 12619 It is proposed that an initial confirmatory sampling assessment be undertaken to assess whether any VOC is emited via this LEV, and if no VOC is identified then no further monitoring be undertaken.
A40 | LEV-A-04S | Area LEV | Area A - Injection | Battery filling with electrolyte - Injection Systems | None | Central Core | 33m Terminates 3m above roof | 0.63 | 14 | 15660 | VOC Vapour from Electrolyte processing containing Diethyl Carbonate (DEC) Ethylene Carbonate (EC) Ethyl Methyl Carbonate (EMC) Assess as TVOC at <20 mg/m³ | 20 | 0.3132 | Volatile Components of Electrolyte i.e. Diethyl Carbonate (DEC) (3 - 10% of electrolyte) Ethylene Carbonate (EC) (20 - 30% of electrolyte) Ethyl Methyl Carbonate (EMC) (50 - 60% of electrolyte) | TVOC with a mass emission rate of >100g/h 1 - 20 mgC/Nm³ | Emission level is <10 kgC/hour Periodic sampling for TVOC once per year EN 12619
A41 | LEV-A-05S | Area LEV | Area A - Injection (Cromex Kit) | Battery filling with electrolyte - Injection Systems | None | Central Core | 33m Terminates 3m above roof | 0.5 | 11.3 | 8010 | VOC Vapour from Electrolyte processing containing Diethyl Carbonate (DEC) Ethylene Carbonate (EC) Ethyl Methyl Carbonate (EMC) Assess as TVOC at <20 mg/m³ | 20 | 0.1602 | Volatile Components of Electrolyte i.e. Diethyl Carbonate (DEC) (3 - 10% of electrolyte) Ethylene Carbonate (EC) (20 - 30% of electrolyte) Ethyl Methyl Carbonate (EMC) (50 - 60% of electrolyte) | TVOC with a mass emission rate of >100g/h 1 - 20 mgC/Nm³ | Emission level is <10 kgC/hour Periodic sampling for TVOC once per year EN 12619
Note that the detailed design of the South plant has not yet been completed, and AESC engineering have not been able to provide any data on the specific plant layout, stack location, stack diomensions or emissions profiles, as they are still awaiting such data from the design contractor.So the data below has been prepared as a reasonable estimate of the likely emissions based on the limited data available.
This data has been prepared subject to the folowing asumptions:
1) the South Plant is assumed to be broadly identical to the North Plant in terms of the activities undertaken and the likely emission sources.
2) AESC has advised that the South Plant is likely to produce around 35% of the overall site output with 65% generated by the North Plant. However, to provide a conservative assessment of potential air quality impacts, it has been assumed that the emissions to air from the South Plant wil be equivalent to the North Plant i.e. an overestimate of total emissions of around 30%.
3) The number of emission points and their dimensions, the emissions flow and concentrations and the plant systems they serve, have been assumed to be identical to those for the North Plant.
4) The locations for the Emission points on the South Plant have been assumed to mirror across from the North Plant, with minor adjustments made when other structures would require the location to be slightly adjusted.
5) The locations of the vents from the glue modules on the South Plant (A36 - A39) have been estimated.

## Materials Data
Solvents
Acronym | Material | CAS | Use | Data
NMP | N-methyl-2-pyrrolidone | 872-50-4 | Cathode production only | H360D so CMR 1 Vapour pressure 0.32hPA at 20°C VOC NOAEC ( Inhalation Repoeat dose) 500 mg/m³ NOAEC (reproduction toxicity) 206 mg/m³ Assess as TVOC
IPA | Isopropyl Alcohol (Propan-2-ol) | 67-63-0 | plant cleaning | Not CMR Vapour Presure 6.02kPA at 25°C VOC NOAEC 5,000ppm DNEL 1,000 mg/m³
Acetone | Acetone |  | plant cleaning | Not CMR Vapour Presure 240 hPA at 20°C VOC NOAEC 22,500ppm DNEL 1,210 mg/m³
Electrolyte
| #VALUE! | Vapour Presure = 1.81 - 2.29 kPa @25°C Thus categorised as VOC
Component of Electrolyte | CAS | EC | % | Risk Phrases | CMR? | Vapour Pressure | VOC? | Include in air emissions Assessment
Ethyl Methyl Carbonate (EMC) Carbonic acid, ethyl methyl ester | 623-53-0 | 433-480-9 | 50 - 60 | Flam. Liq. 2, H225 |  | 4300 Pa @25°C | Yes | Yes
Ethylene carbonate (EC) | 96-49-1 | 202-510-0 | 20 - 30 | Acute Tox. 4 (oral), H302 Eye Irrit. 2, H319 STOT RE 2, H373 |  | 1 hPa @20°C | Yes | Yes
Lithium hexafluorophosphate(1-) | 21324-40-3 | 244-334-7 | 10 - 20 | Acute Tox. 3 (Oral), H301 Skin Corr. 1A, H314 Eye Dam. 1, H318 STOT RE 1, H372 |  | No Data - (only present in solution) | No | No - not VOC
Diethyl carbonate (DEC) | 105-58-8 | 203-311-1 | 3 - 10 | Flam. Liq. 2 H226 |  | 14.4 hPa @25°C | Yes | Yes
Lithium bis(fluorosulfonyl)amide CAS-No.: 171611-11-3 | 171611-11-3 | 686-526-7 | 0.5 - 4 | Acute Tox. 4 (oral), H302 Skin Irrit. 2, H315 Eye Dam. 1, H318 Repr. 2, H361 |  | 27.2Pa @20°C | Yes - Just over 0.01kPa | No - very low Vapour pressure, and only present at very low percentages in the electrolyyte
1,3-Propanesultone | 1120-71-4 | 214-317-9 | 0.1 - 0.8 | Acute Tox. 4(oral),H302 Acute Tox. 4(dermal),H312 Carc. 1B,H350 | CMR1 | 0.0001Pa @25°C | No | No - not VOC
1,3,2-Dioxathiolane, 2,2-dioxide | 1072-53-3 | 600-809-4 | 0.1 - 3 | Acute Tox. 4 (Oral), H302 Skin Corr. 1, H314 Skin Sens. 1B, H317 Eye Dam. 1, H318 Carc. 2, H351 | CMR2 | 0.91Pa @20°C | No | No - not VOC
Vinylene carbonate | 872-36-6 | 212-825-5 | 0.1 - 3 | Acute Tox. 3 (dermal), H311 Skin Irrit. 2, H315 Eye Dam. 1, H318 Skin Sens. 1, H317 STOT RE 2, H373 Aquatic Chronic 2, H411 |  | 335Pa @25°C | Yes | No - low Vapour pressure, and only present at very low percentages in the electrolyte
Glues
Glues | Use | General Comments | Active Components |  | CAS | EU | GHS Risks related to air emissions | Vapour Pressure | VOC?
Compression Glue TB 3082F | light curing adhesive |  | Urethane Acrylate | 25 - 50% |  |  | Not Classified
| Viscous Paste |  | 2-(2-ethoxyethoxy) Ethyl acrylate | 25 - 50% | 7328-17-8 | 230-811-7 | None | 7.4 PA | Not VOC
|  |  | Poly(propylene glycol) | 25 - 50% | 25322-69-4 | 500-039-8 | Not Classified | 0.000839 hPA | Not VOC
|  |  | 2-Propenoic acid, reaction products with dipentaerythritol | >1 - 2.5% | 1384855-91-7 | 800-838-4 | None | 0Pa | Not VOC
|  |  | 2-hydroxy-2-methylpropiophenone | >1 - 2.5% | 7473-98-5 | 231-272-0 | None | 0.0006 hPa | Not VOC
Structure Glue Hardener Betaforce CB-2 | curative adhesive | H351 CMR2 | 4,4'-methylenediphenyl diisocyanate | >20 - 30% | 101-68-8 | 202-966-0 | inhalation ATE 1.5 mg/l dust / mist Resp Sens 1 - H334 Carc 2 - H351 | 0.001Pa | Not VOC
Solid Paste
Structure Glue Resin Betaforce CB-2 | curative adhesive | Not Hazardous | Glycerol propylene oxide | <5% | 25791-96-2 |  |  | 0.003 Pa | Not VOC
| Solid Paste |  | polymer
Thermal Glue Cemedine SX1505 (Base Resin) | Modified silicone polymer based elastic adhesive | Not Classified for health or Env hazards | Aluminium oxide | 40 - 50% | 1344-28-1 |  | N/A - only applies to material in respirable dust form | N/A | Not VOC
| Resin |  | Petroleum | 1 - 5% | 64742-47-8 |  | Asp tox 1 | <1 - 3.7kPa | VOC
| Liquid |  | Resin |  |  |  | Not Classified
Thermal Glue Cemedine SX1505 (Hardener) | Modified silicone polymer based elastic adhesive | Not Classified for health or Env hazards | Aluminium Oxide | 40 - 50% |  |  | N/A - only applies to material in respirable dust form | N/A | Not VOC
| Hardener |  | Alkoxysilane | 1 - <3% |  |  | No Data | Expected to be <0.01Kpa | No data but unlikely to be a significant VOC source
| liquid |  | Organic tin compounds | 0.1 - <1% |  |  | No Data |  | Not VOC
|  |  | Vinyl Silane | 0.1 - <1% |  |  | None |  | No data but unlikely to be a significant VOC source